## bus
| name | vn_kv | type | zone | in_service
0 | Bus 0 | 110 | b | CIGRE_MV | TRUE
1 | Bus 1 | 20 | b | CIGRE_MV | TRUE
2 | Bus 2 | 20 | b | CIGRE_MV | TRUE
3 | Bus 3 | 20 | b | CIGRE_MV | TRUE
4 | Bus 4 | 20 | b | CIGRE_MV | TRUE
5 | Bus 5 | 20 | b | CIGRE_MV | TRUE
6 | Bus 6 | 20 | b | CIGRE_MV | TRUE
7 | Bus 7 | 20 | b | CIGRE_MV | TRUE
8 | Bus 8 | 20 | b | CIGRE_MV | TRUE
9 | Bus 9 | 20 | b | CIGRE_MV | TRUE
10 | Bus 10 | 20 | b | CIGRE_MV | TRUE
11 | Bus 11 | 20 | b | CIGRE_MV | TRUE
12 | Bus 12 | 20 | b | CIGRE_MV | TRUE
13 | Bus 13 | 20 | b | CIGRE_MV | TRUE
14 | Bus 14 | 20 | b | CIGRE_MV | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | Load R1 | 1 | 14.994 | 3.0447 | 0 | 0 | 15.3 | 1 | TRUE | wye
1 | Load R3 | 3 | 0.27645 | 0.069285 | 0 | 0 | 0.285 | 1 | TRUE | wye
2 | Load R4 | 4 | 0.43165 | 0.10818 | 0 | 0 | 0.445 | 1 | TRUE | wye
3 | Load R5 | 5 | 0.7275 | 0.18233 | 0 | 0 | 0.75 | 1 | TRUE | wye
4 | Load R6 | 6 | 0.54805 | 0.13735 | 0 | 0 | 0.565 | 1 | TRUE | wye
5 | Load R8 | 8 | 0.58685 | 0.14708 | 0 | 0 | 0.605 | 1 | TRUE | wye
6 | Load R10 | 10 | 0.4753 | 0.11912 | 0 | 0 | 0.49 | 1 | TRUE | wye
7 | Load R11 | 11 | 0.3298 | 0.082656 | 0 | 0 | 0.34 | 1 | TRUE | wye
8 | Load R12 | 12 | 14.994 | 3.0447 | 0 | 0 | 15.3 | 1 | TRUE | wye
9 | Load R14 | 14 | 0.20855 | 0.052268 | 0 | 0 | 0.215 | 1 | TRUE | wye
10 | Load CI1 | 1 | 4.845 | 1.5925 | 0 | 0 | 5.1 | 1 | TRUE | wye
11 | Load CI3 | 3 | 0.22525 | 0.1396 | 0 | 0 | 0.265 | 1 | TRUE | wye
12 | Load CI7 | 7 | 0.0765 | 0.04741 | 0 | 0 | 0.09 | 1 | TRUE | wye
13 | Load CI9 | 9 | 0.57375 | 0.35558 | 0 | 0 | 0.675 | 1 | TRUE | wye
14 | Load CI10 | 10 | 0.068 | 0.042143 | 0 | 0 | 0.08 | 1 | TRUE | wye
15 | Load CI12 | 12 | 5.016 | 1.6487 | 0 | 0 | 5.28 | 1 | TRUE | wye
16 | Load CI13 | 13 | 0.034 | 0.021071 | 0 | 0 | 0.04 | 1 | TRUE | wye
17 | Load CI14 | 14 | 0.3315 | 0.20545 | 0 | 0 | 0.39 | 1 | TRUE | wye

## switch
| bus | element | et | type | closed | name | z_ohm | in_ka
0 | 6 | 12 | l | LBS | TRUE |  | 0
1 | 7 | 12 | l | LBS | FALSE | S2 | 0
2 | 4 | 13 | l | LBS | FALSE | S3 | 0
3 | 11 | 13 | l | LBS | TRUE |  | 0
4 | 8 | 14 | l | LBS | FALSE | S1 | 0
5 | 14 | 14 | l | LBS | TRUE |  | 0
6 | 0 | 0 | t | CB | TRUE |  | 0
7 | 0 | 1 | t | CB | TRUE |  | 0

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service | s_sc_max_mva | s_sc_min_mva | rx_min | rx_max
0 |  | 0 | 1.03 | 0 | 1 | TRUE | 5000 | 5000 | 0.1 | 0.1

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | Line 1-2 | CABLE_CIGRE_MV | 1 | 2 | 2.82 | 0.501 | 0.716 | 151.1749 | 0 | 0.145 | 1 | 1 | cs | TRUE
1 | Line 2-3 | CABLE_CIGRE_MV | 2 | 3 | 4.42 | 0.501 | 0.716 | 151.1749 | 0 | 0.145 | 1 | 1 | cs | TRUE
2 | Line 3-4 | CABLE_CIGRE_MV | 3 | 4 | 0.61 | 0.501 | 0.716 | 151.1749 | 0 | 0.145 | 1 | 1 | cs | TRUE
3 | Line 4-5 | CABLE_CIGRE_MV | 4 | 5 | 0.56 | 0.501 | 0.716 | 151.1749 | 0 | 0.145 | 1 | 1 | cs | TRUE
4 | Line 5-6 | CABLE_CIGRE_MV | 5 | 6 | 1.54 | 0.501 | 0.716 | 151.1749 | 0 | 0.145 | 1 | 1 | cs | TRUE
5 | Line 7-8 | CABLE_CIGRE_MV | 7 | 8 | 1.67 | 0.501 | 0.716 | 151.1749 | 0 | 0.145 | 1 | 1 | cs | TRUE
6 | Line 8-9 | CABLE_CIGRE_MV | 8 | 9 | 0.32 | 0.501 | 0.716 | 151.1749 | 0 | 0.145 | 1 | 1 | cs | TRUE
7 | Line 9-10 | CABLE_CIGRE_MV | 9 | 10 | 0.77 | 0.501 | 0.716 | 151.1749 | 0 | 0.145 | 1 | 1 | cs | TRUE
8 | Line 10-11 | CABLE_CIGRE_MV | 10 | 11 | 0.33 | 0.501 | 0.716 | 151.1749 | 0 | 0.145 | 1 | 1 | cs | TRUE
9 | Line 3-8 | CABLE_CIGRE_MV | 3 | 8 | 1.3 | 0.501 | 0.716 | 151.1749 | 0 | 0.145 | 1 | 1 | cs | TRUE
10 | Line 12-13 | OHL_CIGRE_MV | 12 | 13 | 4.89 | 0.51 | 0.366 | 10.0968 | 0 | 0.195 | 1 | 1 | ol | TRUE
11 | Line 13-14 | OHL_CIGRE_MV | 13 | 14 | 2.99 | 0.51 | 0.366 | 10.0968 | 0 | 0.195 | 1 | 1 | ol | TRUE
12 | Line 6-7 | CABLE_CIGRE_MV | 6 | 7 | 0.24 | 0.501 | 0.716 | 151.1749 | 0 | 0.145 | 1 | 1 | cs | TRUE
13 | Line 11-4 | CABLE_CIGRE_MV | 11 | 4 | 0.49 | 0.501 | 0.716 | 151.1749 | 0 | 0.145 | 1 | 1 | cs | TRUE
14 | Line 14-8 | OHL_CIGRE_MV | 14 | 8 | 2 | 0.51 | 0.366 | 10.0968 | 0 | 0.195 | 1 | 1 | ol | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | Trafo 0-1 |  | 0 | 1 | 25 | 110 | 20 | 12.0011 | 0.16 | 0 | 0 | 30 | [7 empty] | FALSE | 1 | 1 | TRUE
1 | Trafo 0-12 |  | 0 | 12 | 25 | 110 | 20 | 12.0011 | 0.16 | 0 | 0 | 30 | [7 empty] | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 7 | 16
1 | 4 | 15
2 | 4 | 13
3 | 4 | 11
4 | 2.5 | 9
5 | 1 | 7
6 | 1 | 3
7 | 8 | 3
8 | 8 | 5
9 | 6 | 5
10 | 4 | 5
11 | 4 | 7
12 | 10 | 15
13 | 10 | 11
14 | 10 | 5

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403
CABLE_CIGRE_MV | 151.1749 | 0.501 | 0.716 | 0.145 | cs
OHL_CIGRE_MV | 10.0968 | 0.51 | 0.366 | 0.195 | ol

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | switch | bus | int64
16 | switch | element | int64
17 | switch | et | object
18 | switch | type | object
19 | switch | closed | bool
20 | switch | name | object
21 | switch | z_ohm | float64
22 | switch | in_ka | float64
23 | ext_grid | name | object
24 | ext_grid | bus | uint32
25 | ext_grid | vm_pu | float64
26 | ext_grid | va_degree | float64
27 | ext_grid | slack_weight | float64
28 | ext_grid | in_service | bool
29 | ext_grid | s_sc_max_mva | float64
30 | ext_grid | s_sc_min_mva | float64
31 | ext_grid | rx_min | float64
32 | ext_grid | rx_max | float64
33 | line | name | object
34 | line | std_type | object
35 | line | from_bus | uint32
36 | line | to_bus | uint32
37 | line | length_km | float64
38 | line | r_ohm_per_km | float64
39 | line | x_ohm_per_km | float64
40 | line | c_nf_per_km | float64
41 | line | g_us_per_km | float64
42 | line | max_i_ka | float64
43 | line | df | float64
44 | line | parallel | uint32
45 | line | type | object
46 | line | in_service | bool
47 | trafo | name | object
48 | trafo | std_type | object
49 | trafo | hv_bus | uint32
50 | trafo | lv_bus | uint32
51 | trafo | sn_mva | float64
52 | trafo | vn_hv_kv | float64
53 | trafo | vn_lv_kv | float64
54 | trafo | vk_percent | float64
55 | trafo | vkr_percent | float64
56 | trafo | pfe_kw | float64
57 | trafo | i0_percent | float64
58 | trafo | shift_degree | float64
59 | trafo | tap_side | object
60 | trafo | tap_neutral | float64
61 | trafo | tap_min | float64
62 | trafo | tap_max | float64
63 | trafo | tap_step_percent | float64
64 | trafo | tap_step_degree | float64
65 | trafo | tap_pos | float64
66 | trafo | tap_phase_shifter | bool
67 | trafo | parallel | uint32
68 | trafo | df | float64
69 | trafo | in_service | bool
70 | bus_geodata | x | float64
71 | bus_geodata | y | int64
72 | bus_geodata | coords | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.13.1 | 2.12.0 | FALSE | FALSE |  | 50 | 1